Code No.: 320356

OR

III-B.Tech II-Semester Examination April, 2003

REFRIGERATION AND AIR CONDITIONING

(Common to Mechanical Engineering, Production Engineering, Mechanical Manufacturing Engineering)

Time: 3 hours					Max.Marks:70

Note:-  1. Answer any five questions

2. All questions carry equal marks

3. Use of thermodynamic property tables and charts of 					     refrigerants and psychometric charts is permitted’

---

1.a)	Name any two principally used refrigerants in vapour compression refrigeration 	system and explain their characteristic properties.

b)	An air cycle refrigeration system working on Bell-coleman cycle draws in air into 	the compressor at 7oc and 1bar. It is compressed to a pressure of 6bar according 	to the law  p1.3=constant.  The compressed air then enters the cooler and gets 	cooled at constant pressure to 27o. It then enters the expander and gets 	isentropically expanded to 1bar. The cool air then enters the refrigerator to pick 	up heat from the products and reaches the state of 7oc and 1bar.  This cycle is 	repeated.  Determine the COP of the system. Also determine per kg mass of air 	circulated, the power required by and the capacity of the system.

2.a)	Explain the construction and working of an evaporative condenser.

b)	Why, instead of an expansion cylinder, a throttle valve is used in the vapour 	compression refrigerating system?  A simple saturated vapour compression cycle 	is employed in a vapour compression refrigerating system which uses R12 as the 	refrigerant. The condenser and evaporator temperatures are 30oc and -20oC 	respectively. Determine the COP of the system.  Also determine per TR the 	mass flow rate of the refrigerant and the power requirement of the system.

3.a)	What are the merits and demerits of capillary tube as an expansion device?

Briefly explain how it is sized.

b)	With a simple schematic diagram explain the working of a practical ammonia-

water vapour absorption refrigeration system.

4.a)	What is “defrosting” ?  Explain anyone method of defrosting.

b)	With a simple diagram explain the working of steam jet refrigeration system.  	What ate its applications?

5.a)	Explain briefly any one method of charging a vapour compression refrigeration 	system.

b)	What is vortex or Hilsch tube refrigeration?  What are its applications?  Briefly 	explain the principle of operation of the same.			Contd…2

Code No.: 320356				-2-				OR

6.a)	What is thermodynamic wet bulb temperature?  Moist air exists at 760mm Hg 	pressure, 30oC dbt and 22oC wbt. Calculate the relative humidity and enthalphy of 	moist air per kg, of dry air?

b)	Briefly explain how control of humidity and temperature is done in air 	conditioning practice.

7.a)	What is “effective temperature” ? What are the factors that influence effective 	temperature?

b)	An air condition in plant conditions air to 25oC dbt and 60% RH and handles 	600cmm of air at that state.  The required state of air is achieved by first cooling 	and dehumifying and then by heating. Outdoor air at 40oC dbt and 45%RH is 	mixed with 60% conditioned air and then sent over the cooling coil.  The ADP of 	the cooling coil is 120C and the bypass factor of the heating oil is 0.3.  Determine 	the capacity of the cooling  coil in tons of refrigeration and the capacity of the 	heating coil in kW.  Also find the by-pass factor of the cooling coil and the 	surface temperature of the heating coil.

8.a)	Explain the concept of “SHF”.  Identify the different cooling loads and categorize 	them into sensible and latent heat loads and state how RSHF, GSHF and ESHF 	are determined

b)	Show with the help of a simple sketch, how with a fixed refrigeration circuit, heat

pump can be used for year round air conditioning.

-----