Code No: 420204

Set No.

1

IV-B.Tech. II-Semester Supplementary Examination, July 2003

POWER SYSTEM RELIABILITY

(Electrical and Electronics Engineering)

Time: 3 hours							        Max. Marks: 80

Answer any Five questions

All questions carry equal marks

- - -

1.a)	An electrical power system has 10 generating units of 30 MW capacity each.  If 	the probability of failure any unit is 0.05, calculate the probability of failure of the 	system to supply a steady load of 200 MW.

b)	In a large system the average number of cable faults per year per 100 km of cable 	is 0.5. What is the probability of not more than one fault occurring in a year on a 	cable 10 km long.

2.a)	A truck has four tyres each with a failure rate of 5x10-5/km.  Calculate reliability 	of the truck against tyre failure for a mission of 1000 km.

b)	What will be the improvement in reliability if one spare tyre is taken on the same 	mission?

3.a)	A system consists of a single component with failure rate  and repair rate .  	From the state space analysis derive an expression for its steady state availability.

b)	A system consists of two components A and B with independent failure and repair 	rates.  From the state space analysis derive expressions for the steady state 	probability of occurrence of each state of the system.  Calculate their values given

A=0.2, A=9.8  ;		B=0.4, B=9.6

4.	A system has four generating units A,B,C and D.  A, B and C have a capacity of 	40 MW each while D has a capacity of 80 MW.  The failure and repair rates are 	0.4/year and 9.6/year.  Obtain the state space model with equal capacity states 	merged.

5.a)	Discuss briefly the salient features of ‘Loss of Load’ and ‘Loss of Energy’ 	methods of calculating the probability of capacity deficiency in a system.

b)	In a general system, for 10% of the days during a given period of observation, the 	peakload is between 30 MW and 40 MW, for 15%, between 40 MW and 50 MW, 	for 25% between 50 MW and 60 MW for 30% between 60 MW And 70 MW and 	for rest of the period, between 70 MW and 80MW.  Calculate LOLP if the 	installed capacity is 100 MW with 5 numbers of 20 MW units with  = 0.4/year 	and =9.6/year.

Contd….2

Code No.:420204				-2-				Set No.1

6.	The data regarding generation capacity states of a system and the connector load 	system are tabulated below.  Assuming the system fails when the load is greater 	than the generating capacity, calculate probability and frequency of failure.

Generation System

State no.	State capacity MW	Availability	Departure	rates/year

i			Ci		      A(Ci)	  +(Ci)	  -(Ci)

1			0		0.0016		    19.2		      0

2			20		0.0384		      9.6		      0.4

3			30		0.0384		      9.6		      0.4

4			50		0.9276		      0		      0.8

Load System

State no.	State capacity MW	Availability	Departure	rates/year

j			Lj		      C(Lj)	  +(Lj)	  -(Lj)

1			40		0.2		      0		      2.5

2			30		0.12		      0		      2.5

3			20		0.08		      0		      2.5

4 low load		0		0.6		      1.67		      0

7.a)	Explain how the effect of changing weather conditions are modeled.

b)	Two identical transmission lines operate in a two weather environment with a 	mean normal weather of 10 days and a mean severe weather duration of 0.15 	days.  The line failure rate is 0.00025/day in normal weather and 0.05/day in 	severe weather.  The repair rate is 1.00/day.  Calculate the probability of double 	failure using weighted average method.

8.	Write short notes on the following:

a) Random variables and their distribution.

b) The state model of a component subject to ‘switching’.

c) Uses of Reliability network.

- - -

Code No: 420204

Set No.

2

IV-B.Tech. II-Semester Supplementary Examination, July 2003

POWER SYSTEM RELIABILITY

(Electrical and Electronics Engineering)

Time: 3 hours							        Max. Marks: 80

Answer any Five questions

All questions carry equal marks

- - -

1.a)	Explain the difference between the failure density function f(t) and the hazard 	function h(t).

b)	The hazard of a component with Weibull distribution has =0.5 and =0.95/hr.  	Find the reliability of the component for a mission time of 100 hrs.

2.a)	Derive the relation between the Reliability function (R(t)) and the Mean Time to 	Failure (MTTF) of a component.

b)	Show that for exponential distribution, MTTF is the reciprocal of the failure rate 	.

c)	A component has MTTF of 950 hours.  What is its reliability for a mission time of 	100 hours?

3.a)	Explain what is meant by ‘Minimal Cutset’ in connection with reliability 	evaluation of a system.

b)	The reliability network of a system is given below.  The figures on components 	indicate their reliabilities.  Calculate the reliability of the system using the method 	of cutsets.

4.	A generating station 3 generators rated for 10MW and a fourth one rated for 	20MW.  The failure and repair rates of each of the 4 units are 0.35/year and 	9.65/year respectively.  Obtain simplified state space model combining equal 	capacity states and obtain the following transmition rate:

(i) From 40MW to 20MW state

(ii) From 10MW to 30MW state.

Contd….2

Code No.:420204				-2-				Set No.2

5.a)	Explain a method for computing the probability of capacity deficiency in a 	generation system.

A power plant has FIVE units of capacity 50MW each with a listed outage rate of 	0.01.  Obtain the capacity outage probability table.  The system load model is 	given below:

6.a)	The parameters relating to generation capacity states and load capacity states of a 	system are tabulated below:

Generation System

State index	Capacity (Ci)(MW)	Availability	Departure	rates/day

i			Ci		      A(Ci)	  +(Ci)	  -(Ci)

1			0		0.0000026	    0.104	        0

2			50		0.0002453	    0.078      	    0.0011

3			100		0.0088474	    0.052      	    0.0022

4			150		0.1415578	    0.026	    0.0033

5			200		0.8493466	      0		    0.0044

Load System

State index	 capacity (MW)	Availability	Departure	rates/day

j			Lj		      A(Lj)	  +(Lj)	  -(Lj)

1			150		0.1		      0		      2

2			140		0.25		      0		      2

3			120		0.10		      0		      2

4 			100		0.05		      0		      2

5			   0		0.5		      2		      0

Calculate:

- The probability of failure of the system.

- The frequency of failure of the system.

The system fails wherever the load exceeds the generating capacity.

Contd….3

Code No.:420204				-3-				Set No.2

7.a)	Describe with state space diagram, the Markov Model of a single transmission 	line under two weather environment.

b)	Explain with state space diagram how the pf and ff of system consisting of two 	independent transmission lines under two weather environment.

8.	Write short notes on the following:

(a) Active units and the effect on the rf and ff of the system.

(b) Reliability evaluation of a interconnected systems.

(c) Failure modes of a circuit breaker.

- - -

Code No: 420204

Set No.

3

IV-B.Tech. II-Semester Supplementary Examination, July 2003

POWER SYSTEM RELIABILITY

(Electrical and Electronics Engineering)

Time: 3 hours							        Max. Marks: 80

Answer any Five questions

All questions carry equal marks

- - -

1.a)	When is a random variable said to be continuous? Discuss the properties of  the density function of such a variable.

b)	Derive an expression for the PDF of a Binomial Distribution.

c)	State circumstances under which it can be approximated by the Exponential distribution.

2.a)	Describe the piecewise linear model of the hazard function of a typical electronic component. Suggest suitable distributions that can be fitted to the various regions of the model.

b)	Discuss the effect of maintenance on the reliability of a system.

3.	A system consists of  two components A and B in series, situated such that when one component is down, the other componenet cannot fail. The failure and repair rates of the components are given below.

A = 0.04/day		µA = 9.6/day

B = 0.06/day		µB = 9.4/day

Apply the Markov Model and calculate the probability of failure of the system.

4.	A generating system consists of two units A and B of 20MW and 30MW capacities with forced outage rates of 0.1 and 0.05 respectively. If the mean repair time of either unit is 30 days, calculate.

a)	Probability and frequency of occurrence of exact capacity state of 30MW.

b)	Probability and frequency of failure of the system if the load is steady at 40MW.

5.a)	Explain the method of calculating the LOLP of a generation system. What are inadequacies of LOLP as an index of unreliability?

b)	A generating system consists of two units of 30MW with  = 0.4 /year and           µ = 9.6/year. The daily peak loads have the following distribution.

Daily peak load(MW)		Number of days as a fraction of total

- 0.3

- 0.4

- 0.2

- 0.1

Estimate the expected number of days in a year in which the daily peak loaded the generation capacity.

Contd…..2

Code No:420204				-2-				Set No:3

6.	Two power systems A and B with their margin states as shown below are interconnected by a tie line of 20 MW.

System A				System B

Ma(MW)	A(Ma)			M3	  A(M3)

-40		0.000028		-30	0.000032

-30		0.001385		-20	0.000295

-20		0.003994		-10	0.000572

-10		0.009600		0	0.001575

0		0.013165		10	0.011257

10		0.011501		20	0.215326

20		0.221184		30	0.770942

30		0.652743

Calculate:

a)	The probability of failure of system A without the tie line.

b)	The probability of failure of system A with the tie line which is failure proof.

c)	Repeat (b) if the tie line has a forced outage rate of 0.04 and a failure rate of 0.04/year.

7.a)	Describe the 3 state modes of a transmission line section subject to switching.

b)	Explain what is meant by action events and explain how the probability of these events can be evaluated.

8.	Write short notes on the following:

a)	Merging of equal capacity states of a generation systems.

b)	Stochastic models of load on a system.

c)	Common mode failures and the modeling.

^^^

Code No: 420204

Set No.

4

IV-B.Tech. II-Semester Supplementary Examination, July 2003

POWER SYSTEM RELIABILITY

(Electrical and Electronics Engineering)

Time: 3 hours							        Max. Marks: 80

Answer any Five questions

All questions carry equal marks

- - -

1.a)	Given that the probability of success in a Bernoulli trial is ‘P’, derive an expression for the probability of occurrence of ‘r’ successes out of ‘n’ trials.

b)	A generating station has 5 units each of 20 MW capacity. The probability of failure of any unit is 0.06. If the load on the station is 70 MW what is the probability of the load not being supported.

2.a)	Explain the construction and use of a Reliability network.

b)	The reliability network of a system is given below. The figure on each component indicates its reliability. Calculate the reliability of the system.

3.a)	State and explain the fundamental assumptions of a Markov Process.

b)	For the system shown below, obtain the time domain expression and the steady state values of probabilities P1(t)  and P2(t)

4.a)	Obtain the state space model for a system with 4 identical generating units each having a failure rate  and a repair rate µ.

b)	Consider system with 4 generating units A,B,C and D.  A, B and C have each a capacity of 20MW and the capacity of D is 40MW.  Each of the units has=0.4/year and µ=9.6/year.  Draw the state space model after merging states of identical capacities.

Contd…..2

Code No:420204				-2-				Set No:4

5.a)	Briefly explain the Loss of Energy method.

b)	A power station has 5 generating units of 20 MW capacity with =0.2/year and µ=9.8/year.  The load on the station is distributed as below:

% time for  which

the load occurred		     Load MW

10%				30

15%				40

25%				50

30%				60

20%				70

Find Loss of Energy per year.

6.	The parameters relating to Generation Capacity states and load capacity states of a system are tabulated below:

Generation system

State Number	    Capacity MW	Availability	Departure	rates/day

i		             Ci		     A(Ci)	+(Ci)		-(Ci)

1			0		0.0000026	0.104		    0

2			50		0.0002458	0.078		0.0011

3			300		0.0088474	0.052		0.0022

4			150	            0.1415578	0.026		0.0033

5			200	            0.8493466	   0		0.0044

Load system

State Number	    Load Capacity

StateMW  		Availability	Departure	rates/day

j		           Lj		     A(Lj)	+(Lj)		-(Lj)

1			150		       0.1	   0	    	   2

2			140		       0.25	   0		   2

3			120		       0.10	   0		   2

4			120	                   0.05	   0		   2

5			  0	                   0.5	   2		   0

Calculate:

(a) Probability of failure  (b) Frequency of failure.

Contd…..3

Code No:420204				-3-				Set No:4

7.a)	A load is served by two independent transmission lines A and B under two weather environment.  Draw the state space diagram and explain how the probability of failure of power supply to the load can be calculated.

b)	Two transmission lines A and B with N=2x10-4/day in normal weather and w=5x10-2/day in severe weather and with repair rate µ=1/day in both the weathers supply a load.  The mean duration of normal weather is 10days and that of severe weather 0.1 day.  Calculate the probability of failure of supply to the load.

8.	Write short notes on the following:

(a) Modelling of a circuit breaker.

(b) The Markov model and its application to reliability evaluation.

(c) Binomial distribution.

- - -